## Sayfa1
Single Phase Transformer Design
Inputs |  |  |  | Results
Primary Voltage | = | 34.5 | kV | Dimensions |  |  |  | Efficiency & Loss Analysis
Secondary Voltage | = | 25 | kV | Primary Number of Turns, Np | = | 1490 | turns | Primary Winding Resistance, Rp | = | 6.7655 | Ω
Secondary Number of Turns, Ns | = | 1080 | turns | Secondary Current, Is | = | 20 | A | Secondary Winding Resistance, Rs | = | 3.626 | Ω
Rating of Transformer | = | 500 | kVA | Primary Current, Ip | = | 14.7885 | A | Primary Copper Loss | = | 1.4796 | kW
Peak Flux Density in Core, Bmax | = | 1.5 | T | Core Cross Section Area | = | 695.3262 | cm2 | Secondary Copper Loss | = | 1.4504 | kW
Operating Frequency | = | 50 | Hz | Width of Core, x | = | 26.369 | cm | Total Copper Loss | = | 2.93 | kW
Current Density, J | = | 3 | A/mm2 | Primary Wire Cross Section Area | = | 4.9295 | mm2 | Core Loss | = | 2.6974 | kW
Maximum Ambient Temperature | = | 50 | °C | Secondary Wire Cross Section Area | = | 6.6667 | mm2 | Total Loss | = | 5.6274 | kW
Fill Factor | = | 0.3 |  | Window Area | = | 484.8322 | cm2 | Efficiency | = | 98.887 | %
Density of Core | = | 7650 | kg/m3 | Core Inner Length, Linner | = | 22.0189 | cm
Density of Copper | = | 8960 | kg/m3 | Core Outer Length, Lcore | = | 74.757 | cm | Inductance Calculation
Core Loss | = | 2.62 | W/kg |  |  |  |  | Reluctance of Core | = | 26688.2821 | 1/H
Power Factor | = | 1 |  | Weight Analysis |  |  |  | Magnetizing Inductance, Lm | = | 83.1863 | H
Relative Permeability of Core | = | 830 |  | Total Length of Primary Winding | = | 1749.6771 | m | Primary Base Impedance | = | 2332.89 | Ω
Copper Cost | = | 10 | $/kg | Mass of Primary Winding | = | 77.2804 | kg | Primary Leakage Inductance | = | 148.5164 | mH
Core Material Cost | = | 3 | $/kg | Total Length of Secondary Winding | = | 1268.2223 | m | Secondary Leakage Inductance | = | 78.0278 | mH
Current Exchange Rate | = | 3.9 | ₺/$ | Mass of Secondary Winding | = | 75.7551 | kg
|  |  |  | Total Copper Mass | = | 153.0356 | kg | Cost Analysis
|  |  |  | Core Volume | = | 0.13458 | m3 | Core Cost | = | 12045.7282 | ₺
|  |  |  | Core Mass | = | 1029.5494 | kg | Copper Cost | = | 5968.3874 | ₺
|  |  |  | Total Mass | = | 1182.585 | kg | Total Cost | = | 18014.1155 | ₺
Core Material Datasheet